## main
S.No | Dt. | Sub | ID | From (HH:MM) | To (HH:MM) | Circle | Volt Level | Grid Name | Feeder/ Equip | Feeder or Equip Name/ PTR No | Tripping Details | Load in MW | Load Backfeed on (HH:MM) | Reason of Tripping | Corrective Action Taken | Target Date for Corrective Action | ATR Status as on 24th Apr 2021 | Deptt
| 21-May-21 |  | B21052100030 | 11:17 | 13:26 | South | S_220KV | Okhla | OG_33KV_CKT_1 | OKHL2 CKT-2 | tripped off on diffrencial 0.8 km | 10.65 | 11:19 | FaultSuspected
| 22-May-21 | A | B22052100028 | 1:15 | 15:40 | West | W_220KV | NJF_220KV | OG_66KV_CKT_7 | BODELLA2 CKT-1 | Tripped off on Distance protection ZONE-1 R PHASE 3.5KM |  |  | FaultSuspected
| 22-May-21 | B |  | 1:15 | 15:40 | West | W_66KV | Bodella_2 | ICm_66KV_Feeder_3 | CKT 1 NAJABGARH | Tripped off on O/C |  |  | FaultSuspected
| 22-May-21 |  | B22052100029 | 1:15 | 6:55 | West | W_66KV | Nangloi | ICm_66KV_Feeder_17 | DJB NILOTHI | Tripped off on E/F |  |  | FaultSuspected
| 22-May-21 |  | B22052100030 | 1:16 | 8:02 | West | W_220KV | NJF_220KV | OG_66KV_CKT_7 | NANGLOI | Tripped off on Distance protection ZONE-2 R PHASE 11 KM | 5.8 | 1:26 | FaultSuspected
| 22-May-21 | A | NA | 1:19 | 2:36 | West | W_66KV | DJB_Najafgarh | ICm_66KV_Feeder_16 | 220 Najafgarh CKT-1 | Tripped off on master 86 relay.O/C |  |  | FaultSuspected
| 22-May-21 | B |  | 1:19 | 16:58 | West | W_66KV | DJB_Najafgarh | OGW_66KV_Feeder_16 | G-5 Matiala-CKT-1 | Tripped off on master 86 relay.O/C E/F |  |  | FaultSuspected
| 22-May-21 |  | B22052100033 | 1:28 | 9:56 | West | W_66KV | Pankharoad | OGW_33KV_Feeder_10 | MAYAPURI | Tripped off on E/F |  |  | FaultSuspected
| 22-May-21 | A | B22052100043 | 4:14 | 16:38 | West | W_66KV | DJB_Najafgarh | OGW_66KV_Feeder_16 | G-5 Matiala-CKT-2 | Tripped off on O/C & E/F |  |  | FaultSuspected
| 22-May-21 | B |  | 4:14 | 5:05 | West | W_66KV | DJB_Najafgarh | BUS_COUPLER_71 | 66KV BUSCUPLER_1 | Tripped off on O/C & E/F |  |  | FaultSuspected
| 22-May-21 |  | B22052100050 | 6:23 | 7:35 | South | S_66KV | Malviya_Nagar | OG_33KV_Feeder_31 | TUGHLAKABAD | Tripped off on master 86 relay. | 6.75 | 6:27 | FaultSuspected
| 23-May-21 |  | B23052100036 | 19:38 | 20:00 | West | W_66KV | Sagarpur | ICm_66KV_Feeder_7 | I/C 220KV PPK-3 | Tripped off on O/C & M-86 RELAY | 6.8 | 19:39 | FaultSuspected
| 24-May-21 | A | B24052100066 | 18:56 | 20:45 | South | S_66KV | Malviya_Nagar | IC_66KV_Feeder_31 | MEHRAULI CKT-2 | Tripped off on Gen-1, Zone-1, Gr-2 Relay | 12.8 | 18:56 | BirdageReported
| 24-May-21 | B |  | 18:56 | 20:45 | South | S_220KV | Mehrauli | OG_66KV_CKT_5 | MALVIYA NGR CKT-2 | Tripped off on E/F, Distance protection, B-PHASE, 8.2KM |  |  | BirdageReported
| 24-May-21 |  | B24052100011 | 10:40 | 12:25 | West | W_66KV | Nangloi | OGW_33KV_Feeder_17 | Paschim puri-1 | Tripped off on O/C RELAY | NIL | NIL | FaultSuspected
| 24-May-21 |  | B24052100067 | 18:43 | 23:59 | West | W_33KV | SUDRSHAN_PARK | OG_33KV_CKT_100 | VISHAL CKT | Tripped off on master 86 relay. | NIL | NIL | FaultSuspected
| 25-May-21 | A | B25052100003 | 5:08 | 7:16 | West | W_220KV | NJF_220KV | OG_66KV_CKT_7 | NANGLOI | Tripped off on ZONE-1 B PHASE 5.9 KM ,E/F RELAY | 12.4 | 5:13 | FaultSuspected
| 25-May-21 | B |  | 5:08 | 7:16 | West | W_66KV | Nangloi | ICm_66KV_Feeder_17 | 220KV Najafgarh | Tripped off without indication. |  |  | FaultSuspected
| 25-May-21 |  | B25052100005 | 7:55 | 10:33 | WEST | W_220KV | NJF_220KV | OG_66KV_CKT_7 | NANGLOI WATER WORKS | Tripped off on M- 86 , DISTANCE PROTECTION ZONE 1, B PHASE 1.2 KM RELAY | 11.1 | 7:56 | FaultSuspected
| 25-May-21 | [8 empty] | NIL |  |  |  | NIL
| 27-May-21 |  | B27052100025 | 12:50 | 15:40 | South | S_220KV | Mehrauli | OG_66KV_CKT_5 | IOC bijwasan | Tripped off on E/F | 22 | 12:55 | FaultSuspected
| 27-May-21 |  | B27052100045 | 20:45 | 22:58 | West | W_66KV | Nangloi | OGW_66KV_Feeder_17 | DJB NILOTHI | Tripped off on O/C & E/F | 10.5 | 20:48 | FaultSuspected

## trip_count
Date | Count
21-May-21 | 1
22-May-21 | 10
23-May-21 | 1
24-May-21 | 4
25-May-21 | 3
25-May-21 | 1
27-May-21 | 2
Total