## main
S.No | Dt. | Sub | ID | From (HH:MM) | To (HH:MM) | Circle | Volt Level | Grid Name | Feeder/ Equip | Feeder or Equip Name/ PTR No | Tripping Details | Load in MW | Load Backfeed on (HH:MM) | Reason of Tripping | Corrective Action Taken | Target Date for Corrective Action | ATR Status as on 24th Apr 2021 | Deptt
| 01-May-21 |  | B01052100007 | 6:37 | 9:58 | South | S_66KV | Palam_66KV | IC_66KV_Feeder_40 | Brijwasan | E/F,HIGH SET/LOWSET,M-86 | NIL | NIL | FaultSuspected
| 01-May-21 | A | B01052100053 | 18:45 | 21:08 | South | S_220KV | Vasantkunj | OG_66KV_CKT_4 | VASANT KUNJ C-1 | WITHOUT INDICATION | NIL | NIL | FaultSuspected
| 01-May-21 | B | B01052100054 | 18:45 | 21:08 | South | S_220KV | Vasantkunj | OG_66KV_CKT_4 | VASANT KUNJ C-2 | WITHOUT INDICATION | NIL | NIL | FaultSuspected
| 02-May-21 |  | B02052100006 | 5:30 | 7:01 | West | W_66KV | Paschimvihar | OGW_33KV_Feeder_11 | MUKHERJEE PARK CKT 3 T-OFF CHUKHANDI | Tripped off on R,Y & B PHASE ZONE-4, DISTANCE PROTECTION, M-86 RELAY | 3.3 | 5:33 | FaultSuspected
| 02-May-21 |  | B02052100025 | 13:40 | 13:48 | West | W_66KV | Bodella_2 | IC_11KV | 11KV I/C -2 | Tripped off on O/C RELAY | 8.4 | 13:45 | NoAbnormalityFound
| 03-May-21 |  | B03052100001 | 5:35 | 8:50 | West | W_220KV | PeeraGarhi_220KV | OG_33KV_CKT_8 | PaschimPuri_CKT1 (PASCHIM VIHAR T-OFF PASCHIM PURI-1) | Tripped off on Y PHASE Z-1, 1.2KM DISTANCE RELAY | 4.5 | 5:38 | FaultSuspected
| 03-May-21 |  | B03052100039 | 16:22 | 20:05 | West | W_66KV | Pankharoad | PTRW_10 | PowerTransformer_20MVA_3 ALONG WITH I/C - 3 | Tripped off on master 86 relay. | 7.8 | 16:25 | FaultSuspected
| 03-May-21 |  | B03052100023 | 12:20 | 12:38 | South | S_66KV | MCIE | IC_11KV | 11KV I/C -3 | Tripped off on master 86 & Lockout relay. | 8 | 12:38 | FaultSuspected
| 04-May-21 |  | B04052100004 | 2:35 | 4:29 | West | W_66KV | Bodella_1 | OGW_66KV_Feeder_2 | CKT 2 PASHIM VHR | Tripped off on O/C & E/F Relay. | NIL | NIL | FaultSuspected
| 04-May-21 |  | B04052100012 | 7:45 | 15:07 | South | S_33KV | DC_Saket | PTR_5 | PowerTransformer_20MVA_3 Along with 11KV I/C-3 | Tripped off on E/F, M-86 relay & I/C-M-86 relay. | 5.6 MW | 7:50 | FaultSuspected
| 05-May-21 |  | B05052100005 | 7:41 | 13:10 | South | S_66KV | JNU | OG_33KV_Feeder_30 | O/G RKPURAM1 | DISTANCE PROTECTION,O/C | 2.2 | 7:45 | FaultSuspected
| 05-May-21 |  | B05052100008 | 10:30 | 16:25 | West | W_220KV | PPK2_220KV | OG_66KV_CKT_9 | Hastal Ckt-1 | DISTANCE PROTECTION,B PHASE 4.4 KMS | 12 | 10:48 | FaultSuspected
| 05-May-21 |  | B05052100036 | 20:36 | 23:08 | West | W_66KV | Nangloi | ICm_66KV_Feeder_17 | NILOTHI | Tripped off on O/C & E/F | 11.7 | 20:38 | FaultSuspected
| 06-May-21 | A | B06052100009 | 6:30 | 8:35 | South | S_66KV | Palam_66KV | PTR_40 | 50 MVA PTR-2 | Tripped off on LOW SET O/C & HIGH SET O/C RELAY | 4.3 | 6:35 | FaultSuspected
| 06-May-21 | B | B06052100011 | 6:30 | 6:35 | South | S_66KV | Palam_66KV | BUS_COUPLER_40 | 33KV BUSCUPLER_1 | Tripped off on O/C RELAY |  |  | NoAbnormalityFound
| 06-May-21 |  | B06052100034 | 15:03 | 15:42 | South | S_66KV | FATHEPUR_BERI | IC_66KV_Feeder_101 | 220KV MEHRAULI CKT -1 BAY NO 22 | Tripped off on differential & M-86 RELAY | 7.2 | 15:04 | NoAbnormalityFound
| 06-May-21 | A | NA | 17:53 | 20:10 | South | S_220KV | Lodhi_Road | OG_33KV_CKT_3 | NIZAMUDDIN | Tripped off on M-86 RELAY | 8.3 | 4.3 MW TIL 17:55 & 4 MW TIL 18:17 | FaultSuspected
| 06-May-21 | B | NA | 17:53 | 21:00 | South | S_33KV | Nizamuddin | PTR_11 | PowerTransformer_20MVA_1 | Tripped off on differential, E/F & O/C RELAY |  |  | FaultSuspected
| 30-Apr-21 |  | B30042100034 | 17:21 | 20:15 | South | S_33KV | Nizamuddin | OG_33KV_Feeder_11 | O/G SUPREME COURT | Tripped off on O/C LOW SET | 1.2 | 17:25 | FaultSuspected

## trip_count
Date | Count
01-May-21 | 3
02-May-21 | 2
03-May-21 | 3
04-May-21 | 2
05-May-21 | 3
06-May-21 | 5
30-Apr-21 | 1
Total